MTX

Model MTX Instantaneous

Master Specification

General

Made in the U.S.A.

Provide a quantity of () packaged type instantaneous marine electric water heater(s) Model No.MTX as manufactured by HUBBELL Electric Heater Co., Stratford, CT. The entire unit is packaged ready for plumbing and electrical service connections and shall be Type Approved by the American Bureau of Shipping (ABS) and bear the cULus listing mark certifying the entire unit to UL499, UL EPH Sanitation listed to ANSI/NSF Standard 5 and CSA C22.2 No. 88. All fabrication and assembly shall be performed in the U.S.A.

Heating Chamber The heating chamber shall be all sil-brazed copper and bronze construction. A plastic heating chamber shall not be acceptable. Water heater heating chamber shall be rated for a maximum allowable working pressure of 150 psi. The heating chamber and all electrical controls shall be completely enclosed in a heavy gauge Type 304 stainless steel case.The water heater shall be rated at ___ KW which will heat ___ GPM of water at ___ °F

rise (__ ° to __ °F ). Heaters that require the use of a flow restrictor or specialized aerator

shall not be acceptable.

Electrical The tankless heater shall be designed to operate at 440 volts, 3 phase, 60Hz balanced power and shall draw equal amperage across all phases at all times. For 3 phase heaters, power shall be a 3 wire (3 live, 1 ground) or a 4 wire (3 live, 1 neutral, 1 ground) system that does not require a neutral leg. The heater will draw ___amps only when operating at full power. The immersion heating elements shall be high quality incoloy sheathed and sized to obtain the rated capacity. Each element is to be operated using zero cross over solid state controls. The heating elements shall be fully modulated from 0-100% to provide precise temperature control through the full range of flows. A Hi-Limit thermostat with automatic reset shall be factory installed to disconnect each heating element in the event of an over-temperature condition. An electronic digital display temperature controller shall be user adjustable in 1° increments in either °F or °C

and shall display flow rate, outlet temperature, inlet temperature and provide error indication. A turbine-type flow meter shall be factory installed to provide precise temperature control for water flows as low as 0.2 GPM up to a maximum flow of 8 GPM. Heaters that require greater than 0.2 GPM flow for actuation or heaters that utilize on/off flow switch technology or restrict flow shall not be acceptable.

Warranty Hubbell shall warranty all electrical components against defects in workmanship and material for a period of one (1) year from date of start-up, and the heating chamber for five (5) years from date of start-up, provided that the unit is installed and operated within the scope of the heater's design and operating capability. Labor is not covered under warranty. Each heater shall be shipped with a complete set of installation and operating instructions including spare parts list and drawing.

Options In addition, the water heater shall be supplied with the following options:

Option

Option

Option

Rev. A