MASTER SPECIFICATION FOR BW MODELS

JOB NAME:_______________________________ 		  ENGINEER:___________________________________

REPRESENTATIVE:_______________________ 		  CONTRACTOR:_______________________________

GENERAL

Provide a quantity of _______ packaged type indirect fired storage heater(s) Model No. _____________________ as manufactured by HUBBELL Electric Heater Co., Stratford, CT.  The pressure vessel shall be mounted on structural supports and be suitably insulated, jacketed, painted, and provided with lifting lugs. The entire unit is to be packaged ready for service connections.

# PRESSURE VESSEL

The pressure vessel shall be all welded construction and ASME Code Section VIII stamped for a working pressure of 125 psi (Optional Specification: ____psi) and contain a minimum of _______ gallons of storage.  The storage vessel hall be carbon steel and lined with seamless Hydrastone Cement to a minimum thickness of 5/8" on 100% of all interior tank surfaces (Optional Specifications: Phenolic lined steel tank, Hot dipped galvanized steel tank, Flame sprayed copper coated steel tank, 3lb/Sq.Ft. Copper lined steel tank, solid Type 304 or 316L stainless steel tank, Solid copper-silicon tank, solid 90/10 Copper-nickel tank).  The pressure vessel is to be completely covered with 2" thick "E" type energy conservation fiberglass blanket insulation and enclosed in a heavy gauge galvanized steel metal jacket finished in gray hammertone enamel.  An ASME approved automatic reseating combination temperature and pressure relief valve set at the tank WP and 210°F shall protect the vessel.

HEATING SECTION

The coil shall be rated to heat __________ GPH from __________°F to _________°F when supplied with _______GPM of boiler water (Optional specification:  HTHW) from ___________°F to ____________°F.  The single wall (Optional specification: double wall) heating coil shall be constructed from 20 gauge, 3/4" O.D. copper tubes (Optional specifications:  90/10 Copper-nickel, admiralty, stainless steel) with all non-ferrous wetted parts and designed for a maximum allowable working pressure of 150psi at 275°F (Optional specification: 400psi at 450°F) maximum temperature.  The coil head shall be fabricated steel.

# CONTROLS

# The water heater controls shall (shall not) be factory assembled and piped.  A self-contained modulating three-way diverting valve regulates the flow of boiler water to the heating coil and diverts unused boiler water back to the loop (Optional specification: ON/OFF modulating valve will regulate the flow of boiler water to the heating coil without diverting back to the boiler, thermostat to provide ON/OFF control of a boiler water pump).

In addition, the water heater may be supplied with the following optional features:

Option  Domestic water dial temperature and pressure gauge shall be factory installed.

Option  The water heater shall be equipped with a factory packaged intra-tank circulator to constantly

circulate water within the tank to reduce stratification.

Option  The heating coil shall be wrapped and baffled and piped with an integral pump package to force

circulate water over the heating coil in order to reduce the coil size.

Option  Single solenoid safety system to close the boiler water supply to the heating coil should the

water temperature in the tank reach the hi-limit set point.  Requires 5 AMP, 120 Volt service.

Option  Double solenoid safety system to close the boiler water supply to the heating water in the storage tank to

drain addition to closing the boiler water supply to the control valve.  Requires 5 AMP, 120 Volt service.

## WARRANTY

The water heater manufacturer shall warranty all components against defects in Workmanship and material for a period of one (1) year from date of start-up, and the pressure vessel for a full five (5) years Non Pro-Rated (Optional Specification: full ten (10) years Non Pro-Rated) from date of start-up, provided that the unit is started within three (3) months of date of shipment and installed and operated within the scope of the tank design and operating capability.  Each water heater shall be shipped with a complete set of installation and operating instructions including a spare parts list and approved drawing.