MASTER SPECIFICATION FOR MODEL CE110

JOB NAME:______________________________		ENGINEER:________________________

REPRESENTATIVE:______________________		CONTRACTOR:______________________

Provide a quantity of ______ point-of-use electric water heater(s) Model CE110 (Optional Specification:  Model CE110-450W) as manufactured by HUBBELL Electric Heater Co., Stratford, CT.  The pressure section shall be constructed of stainless steel and rated for 150psi working pressure.  The water heater is designed for installation directly under the plumbing fixture without occupying any floor space.   The tank is to be jacketed with stainless steel and insulated with fiberglass blanket insulation. The immersion copper sheathed heating element shall be rated at 1000 Watts (Optional Specification: 450 Watts), 120 Volt, Single Phase, 60 Hz power and have a maximum rating of 50 Watts per square inch to ensure heating element longevity.  The immersion heater shall be controlled by an adjustable 110-170°F thermostat and will provide hot water at the stated GPH recovery rate regardless of the short-term flow rate at the point-of-use fixture. The water heater shall not require the replacement of the original faucet mounted aerator or the installation of a flow restricting device, and the heater shall be operable from 0-150psi working pressure. The heater shall include an over-temperature manual reset Hi-Limit designed to disconnect all conductors to the heating element in the event of an over-temperature condition.  Water heaters relying solely on an automatic resetting Hi-Limit device will not be acceptable.  Two (2) wall brackets shall be supplied for wall mounting.  An ASME rated combination temperature and pressure safety relief valve set at 150psi and 210°F shall be factory supplied for in the field installation.

In addition, the water heater may be supplied with the following optional feature:

Option:

Tempering Valve to extend the hot water supply 1/2" size, 100-130°F.

Factory supplied 3 foot long grounded power cord

# WARRANTY

The heater manufacturer shall offer a comprehensive full ten (10) year Non Pro-Rated warranty against defects in workmanship and material covering the entire unit including all electrical components and the pressure section, provided that the unit(s) are started within three (3) months of date of shipment and installed and operated within the scope of the unit’s design and operating capabilities.